Suggested Specifications For Onyx Valve

Series CAP Pneumatically Operated Pinch Valves

Valves shall be of cast metal body mechanical pinch type with integral flanges on body and flexible sleeve.  Valve shall be full round, capable of passing a sphere equal to half the diameter of the mating pipe.  All internal metal parts are to be isolated from the process fluid by the flexible rubber sleeve.

Valve housing shall be cast iron ASTM #A-126 CL-35, with flanges drilled to ANSI B16.1 Class 125 standard.  Flanges shall have through holes and shall accommodate a standard hex nut per ANSI B18.2.2; tapped flanges are not acceptable.  All bolts used in valve assembly shall be ASTM A 108 grade B5, zinc plated, 80,000 psi min yield / 100,000 psi min tensile strength.  Valve shall be painted per Steel Structures Painting Council Standard #SSPC-SP1-G3 with (2) coats of black interior/exterior Alkyd Enamel to a total thickness of 5 mils minimum.

The rubber sleeve shall be compression molded to insure consistent wall thickness and de-lamination resistance.  Rubber sleeve shall be reinforced with polyester fabric or nylon cords. The rubber sleeve shall be provided with Positive Opening Tabs to insure full opening after the valve has been closed for extended periods of time; tabs shall be fastened directly to the pinch bar with bolts and nuts.

Valve stem shall be 303-stainless steel.  To prevent galling, the stem shall be guided by a bronze alloy ASTM # B 148-65 9B bearing.  To avoid contaminating the actuator in the event of sleeve failure, the actuator shall be separated from the valve housing assembly by a steel open yoke.  The actuator shall be connected to the valve stem with a bronze coupling.

The valve shall be provided with a fail-open or fail-closed single acting pneumatic actuator capable of operating on 80 to 120 psi compressed air.  Failure mode shall be insured by a simple, reliable spring; failure mechanisms that rely on trapped air are not acceptable.  The actuator shall not have any pistons, piston rings, diaphragms or other high maintenance components.  Actuator should be able to tolerate water, compressor oil, pipe scale, and other air line contaminants without any adverse effects, and should not require filtered air supply.  Actuator shall be provided with permanently lubricated bronze alloy bearings and a 303-stainless steel actuator shaft for zero maintenance operation.  Actuator shall be Onyx Valve Air Bag design or approved equal.

Valves shall be Onyx series CAP or approved equal.