Suggested Specifications For Onyx

Series DHC Manually Operated Pinch Valves

Valves shall be of full cast metal body mechanical pinch type with integral flanges on body and flexible sleeve.  Valve shall be full round, capable of passing a sphere equal to the diameter of the mating pipe.  All internal metal parts are to be isolated from the process fluid by the flexible rubber sleeve.

Valve housing shall be cast iron ASTM #A-126 CL-35, with flanges drilled to ANSI B16.1 Class 125 standard.  Flanges shall have through holes and shall accommodate a standard hex nut per ANSI B18.2.2; tapped flanges are not acceptable.  All bolts used in valve assembly shall be ASTM A 108 grade B5, zinc plated, 80,000 psi min yield / 100,000 psi min tensile strength.  Valve shall be painted per Steel Structures Painting Council Standard #SSPC-SP1-G3 with (2) coats of black interior/exterior Alkyd Enamel to a total thickness of 5 mils minimum.

The rubber sleeve shall be compression molded to insure consistent wall thickness and de-lamination resistance.  Rubber sleeve shall be reinforced with polyester fabric or nylon cords. The rubber sleeve shall be provided with Positive Opening Tabs to insure full opening after the valve has been closed for extended periods of time; tabs shall be fastened directly to the pinch bar with bolts and nuts.

Hand wheel closing mechanism shall be double-acting, and shall pinch the rubber sleeve closed on center line.  Stem shall be 303 stainless steel with ACME class 2G left hand threads.  To prevent gauling, the stem shall be driven by a bronze alloy ASTM # B 148-65 9B drive nut.  The mechanism shall be rigidly supported by 303 stainless steel guide rods supported by  bronze bearings in the top housing, and ultra high molecular weight polyethylene bearings in the bottom housing.  To prevent binding in the event of a sleeve failure, the stem threads shall always remain outside the valve bonnet assembly, and shall be completely isolated from the process fluid, even if the sleeve fails.

Valve shall be designed so that the required one-hand rim pull does not exceed 50 lbf at max rated pressure.

Valves shall be Onyx series DHC or approved equal.